## Overview
Field | Value
-- WIND FARM A - AT A GLANCE --
Wind farm | A (Wind Farm B and C are NOT part of this project)
Number of turbines | 5
Turbine asset IDs | 0, 10, 11, 13, 21
Number of observations (deduplicated) | 425,023
Number of columns | 85
Number of physical sensor columns | 81
Documented base signals | 54
Date range | 2021-12-31 00:00:00 to 2023-11-20 00:40:00
Total span | 689 days (1.89 years)
Sampling interval | 10 minutes
Approx. turbine-years of data | 8.1
Number of event windows / source files | 22
Anomaly (failure) events | 12
Normal (control) events | 10
-- AUTHORITATIVE DATA --
Use for Phase 3 | analysis_data/scada_unique.parquet (425,023 rows) and analysis_data/scada_by_event.parquet (1,196,747 rows)
Do NOT use | cleaned_data/cleaned_scada_data.parquet - it contains 771,542 duplicate (asset_id, timestamp) rows (64.47%)
Excel copies | cleaned_data/excel/ - INSPECTION ONLY, never the pipeline input
-- DATA QUALITY --
Duplicate (turbine, timestamp) rows | 0
Columns with missing values | 2 (sensor_14_avg=7, sensor_22_avg=7)
Constant zero-valued columns | sensor_46, sensor_49 - exclude from modelling
-- SENSOR TYPES ABSENT FROM THIS DATASET --
Vibration / acceleration / acoustic | ABSENT
Pressure (including oil pressure) | ABSENT - only oil temperature exists
Maintenance / work-order records | ABSENT
Turbine metadata (model, capacity, commissioning) | ABSENT - anonymised

## Turbine_Summary
turbine_uid | asset_id | observations | pct_of_total | first_timestamp | last_timestamp | span_days | sampling_interval_min | pct_intervals_exactly_10min | gaps_over_10min | largest_gap_hours | event_windows | anomaly_events | normal_events | event_ids | failure_modes
A0 | 0 | 94578 | 22.25 | 2021-12-31 | 2023-10-22 10:20 | 660 | 10 | 99.971 | 27 | 13 | 5 | 3 | 2 | 0, 24, 26, 71, 73 | Hydraulic group; Generator bearing failure; Hydraulic group
A10 | 10 | 98632 | 23.21 | 2021-12-31 | 2023-11-20 00:40 | 689 | 10 | 99.944 | 55 | 13 | 5 | 3 | 2 | 3, 10, 17, 40, 42 | Generator bearing failure; Hydraulic group; Gearbox failure
A11 | 11 | 76484 | 18 | 2022-04-04 02:30 | 2023-09-21 00:50 | 534 | 10 | 99.973 | 21 | 13 | 4 | 1 | 3 | 25, 68, 69, 92 | Transformer failure
A13 | 13 | 80048 | 18.83 | 2022-03-03 14:00 | 2023-09-13 15:30 | 559 | 10 | 99.968 | 26 | 13 | 4 | 2 | 2 | 14, 38, 45, 84 | Hydraulic group; Hydraulic group
A21 | 21 | 75281 | 17.71 | 2022-04-30 13:20 | 2023-10-21 08:40 | 538 | 10 | 99.942 | 44 | 228.83 | 4 | 3 | 1 | 13, 22, 51, 72 | Hydraulic group; Gearbox failure; Gearbox bearings damaged

## Sensor_Catalog
Column Name | Description | Unit | Data Type | Category | Physical Sensor? | Identifier/Metadata? | Turbine Component | Statistic | Predictive Maintenance Relevance | Documentation Source | Missing Values | Min | Max | Notes
event_id | Source event-window file (filename == event_id) | int | int64 | Metadata | NO | YES | Provenance | value | Event-level evaluation and provenance. NEVER a model feature. | Raw dataset field | 0 | 0 | 92
time_stamp | Timestamp of the 10-minute aggregation interval | datetime | datetime64[ns] | Timestamp | NO | YES | Time index | value | Ordering and time-based splitting ONLY. Never a model feature. | Raw dataset field | 0
asset_id | Turbine identifier as supplied in the raw files | int | int64 | Identifier | NO | YES | Turbine | value | Grouping key. Values: 0, 10, 11, 13, 21. | Raw dataset field | 0 | 0 | 21
row_id_in_event | Per-file row counter; event_info indexes into it | int | int64 | Metadata | NO | YES | Provenance | value | LEAKAGE RISK: restarts at 0 in every file and encodes position inside an event window. Never a feature. | Raw dataset field | 0 | 0 | 56157
train_test | Benchmark split flag of the source event window | string | object | Train/prediction metadata | NO | YES | Metadata | value | LEAKAGE RISK: belongs to an event window, not an observation. 38,406 timestamps carry both values. | Raw dataset field | 0
status_type_id | Operating-status code | int | int64 | Status information | NO | YES | Turbine state | value | LEAKAGE RISK: code meanings NOT DOCUMENTED, and it is a near-perfect proxy for the event label. Permitted ONLY as a filter to select normal-operation rows for training. | Raw dataset field | 0 | 0 | 4
sensor_0_avg | Ambient temperature | degC | float64 | Temperature | YES | NO | Environment | average | MANDATORY CONDITIONING - every temperature must be referenced to ambient. On its own it is seasonal, NOT a fault signal. | feature_description.csv | 0 | 4 | 41
sensor_1_avg | Wind absolute direction | deg | float64 | Wind / orientation | YES | NO | Environment | average | LOW - angular signal. Yaw misalignment affects load. Must not be averaged naively (wraps at 360 deg). | feature_description.csv | 0 | 0 | 359 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_2_avg | Wind relative direction | deg | float64 | Wind / orientation | YES | NO | Environment | average | LOW - angular signal. Yaw misalignment affects load. Must not be averaged naively (wraps at 360 deg). | feature_description.csv | 0 | -180 | 180 | ANGULAR - wraps at 360 deg; do not average or difference naively.
wind_speed_3_avg | Windspeed | m/s | float64 | Wind | YES | NO | Environment | average | MANDATORY CONDITIONING - primary driver of load; used for power-curve deviation. | feature_description.csv | 0 | 0.4 | 26.6
wind_speed_4_avg | Estimated windspeed | m/s | float64 | Wind | YES | NO | Environment | average | MANDATORY CONDITIONING - primary driver of load; used for power-curve deviation. | feature_description.csv | 0 | 0 | 26.6
wind_speed_3_max | Windspeed | m/s | float64 | Wind | YES | NO | Environment | maximum | MANDATORY CONDITIONING - primary driver of load; used for power-curve deviation. | feature_description.csv | 0 | 0.4 | 70
wind_speed_3_min | Windspeed | m/s | float64 | Wind | YES | NO | Environment | minimum | MANDATORY CONDITIONING - primary driver of load; used for power-curve deviation. | feature_description.csv | 0 | 0.4 | 14.6
wind_speed_3_std | Windspeed | m/s | float64 | Wind | YES | NO | Environment | std_dev | MANDATORY CONDITIONING - primary driver of load; used for power-curve deviation. | feature_description.csv | 0 | 0 | 70
sensor_5_avg | Pitch angle | deg | float64 | Pitch | YES | NO | Pitch system | average | MEDIUM - the hydraulic group actuates pitch, so erratic pitch may reflect hydraulic wear. | feature_description.csv | 0 | -2.3 | 90 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_5_max | Pitch angle | deg | float64 | Pitch | YES | NO | Pitch system | maximum | MEDIUM - the hydraulic group actuates pitch, so erratic pitch may reflect hydraulic wear. | feature_description.csv | 0 | -2.2 | 90 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_5_min | Pitch angle | deg | float64 | Pitch | YES | NO | Pitch system | minimum | MEDIUM - the hydraulic group actuates pitch, so erratic pitch may reflect hydraulic wear. | feature_description.csv | 0 | -5 | 90 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_5_std | Pitch angle | deg | float64 | Pitch | YES | NO | Pitch system | std_dev | MEDIUM - the hydraulic group actuates pitch, so erratic pitch may reflect hydraulic wear. | feature_description.csv | 0 | 0 | 45.5 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_6_avg | Temperature in the hub controller | degC | float64 | Temperature | YES | NO | Control cabinet | average | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 11 | 52
sensor_7_avg | Temperature in the top nacelle controller | degC | float64 | Temperature | YES | NO | Nacelle | average | LOW/REFERENCE - internal reference temperature; nose cone tracks ambient closely. | feature_description.csv | 0 | 22 | 59
sensor_8_avg | Temperature in the choke coils on the VCS-section | degC | float64 | Temperature | YES | NO | Control cabinet | average | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 13 | 149
sensor_9_avg | Temperature on the VCP-board | degC | float64 | Temperature | YES | NO | Control cabinet | average | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 25 | 66
sensor_10_avg | Temperature in the VCS cooling water | degC | float64 | Temperature | YES | NO | Control cabinet | average | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 20 | 56
sensor_11_avg | Temperature in gearbox bearing on high speed shaft | degC | float64 | Temperature | YES | NO | Gearbox | average | HIGH - directly targets the 3 gearbox-related anomalies (2 Gearbox failure + 1 Gearbox bearings damaged). | feature_description.csv | 0 | 15 | 72
sensor_12_avg | Temperature oil in gearbox | degC | float64 | Temperature | YES | NO | Gearbox | average | HIGH - directly targets the 3 gearbox-related anomalies (2 Gearbox failure + 1 Gearbox bearings damaged). | feature_description.csv | 0 | 15 | 65
sensor_13_avg | Temperature in generator bearing 2 (Drive End) | degC | float64 | Temperature | YES | NO | Generator bearing | average | HIGH - directly targets the 2 Generator bearing failures. The drive-end minus non-drive-end difference is self-normalising. | feature_description.csv | 0 | 13 | 205
sensor_14_avg | Temperature in generator bearing 1 (Non-Drive End) | degC | float64 | Temperature | YES | NO | Generator bearing | average | HIGH - directly targets the 2 Generator bearing failures. The drive-end minus non-drive-end difference is self-normalising. | feature_description.csv | 20 | 12 | 205
sensor_15_avg | Temperature inside generator in stator windings phase 1 | degC | float64 | Temperature | YES | NO | Generator | average | MEDIUM - generator electrical condition; phase-to-phase divergence indicates a fault. | feature_description.csv | 0 | 14 | 205
sensor_16_avg | Temperature inside generator in stator windings phase 2 | degC | float64 | Temperature | YES | NO | Generator | average | MEDIUM - generator electrical condition; phase-to-phase divergence indicates a fault. | feature_description.csv | 0 | 14 | 205
sensor_17_avg | Temperature inside generator in stator windings phase 3 | degC | float64 | Temperature | YES | NO | Generator | average | MEDIUM - generator electrical condition; phase-to-phase divergence indicates a fault. | feature_description.csv | 0 | 14 | 205
sensor_18_avg | Generator rpm in latest period | rpm | float64 | Speed (rotational) | YES | NO | Generator | average | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 1684.4
sensor_18_max | Generator rpm in latest period | rpm | float64 | Speed (rotational) | YES | NO | Generator | maximum | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 2040.9
sensor_18_min | Generator rpm in latest period | rpm | float64 | Speed (rotational) | YES | NO | Generator | minimum | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 1675.5
sensor_18_std | Generator rpm in latest period | rpm | float64 | Speed (rotational) | YES | NO | Generator | std_dev | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 823.2
sensor_19_avg | Temperature in the split ring chamber | degC | float64 | Temperature | YES | NO | Slip ring / brush gear | average | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 10 | 205
sensor_20_avg | Temperature in the busbar section | degC | float64 | Temperature | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 17 | 77
sensor_21_avg | Temperature measured by the IGBT-driver on the grid side inverter | degC | float64 | Temperature | YES | NO | Converter | average | MEDIUM - converter thermal condition. | feature_description.csv | 0 | 24 | 59
sensor_22_avg | Actual phase displacement | (none given) | float64 | Electrical - power factor | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 20 | 0.2 | 1
sensor_23_avg | Averaged current in phase 1 | A | float64 | Electrical - current | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 1701.8
sensor_24_avg | Averaged current in phase 2 | A | float64 | Electrical - current | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 1 | 1717.6
sensor_25_avg | Averaged current in phase 3 | A | float64 | Electrical - current | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 1 | 1690.5
sensor_26_avg | Grid frequency | Hz | float64 | Electrical - grid | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 50.1
reactive_power_27_avg | Possible grid capacitive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 0.4878 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_27_max | Possible grid capacitive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | maximum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 0.4878 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_27_min | Possible grid capacitive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | minimum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -0.0976 | 0.4878 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_27_std | Possible grid capacitive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | std_dev | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 0.2439 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_28_avg | Possible grid inductive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -0.4878 | 0 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_28_max | Possible grid inductive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | maximum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -0.4878 | 0.0976 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_28_min | Possible grid inductive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | minimum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -0.4878 | 0 | Values are NORMALISED to ~0-1 despite the documented unit.
reactive_power_28_std | Possible grid inductive reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | std_dev | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 0.2439 | Values are NORMALISED to ~0-1 despite the documented unit.
power_29_avg | Possible grid active power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | average | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | 0 | 0.9756 | Values are NORMALISED to ~0-1 despite the documented unit.
power_29_max | Possible grid active power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | maximum | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | 0 | 0.9756 | Values are NORMALISED to ~0-1 despite the documented unit.
power_29_min | Possible grid active power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | minimum | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | 0 | 0.9756 | Values are NORMALISED to ~0-1 despite the documented unit.
power_29_std | Possible grid active power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | std_dev | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | 0 | 0.4876 | Values are NORMALISED to ~0-1 despite the documented unit.
power_30_avg | Grid power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | average | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | -0.0157 | 0.976 | Values are NORMALISED to ~0-1 despite the documented unit.
power_30_max | Grid power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | maximum | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | -0.014 | 1.0344 | Values are NORMALISED to ~0-1 despite the documented unit.
power_30_min | Grid power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | minimum | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | -0.0441 | 0.9749 | Values are NORMALISED to ~0-1 despite the documented unit.
power_30_std | Grid power | kW | float64 | Electrical - active power | YES | NO | Grid / electrical | std_dev | MEDIUM - the load variable. Mandatory conditioning input, and supports power-curve deviation. NOTE: values are normalised to 0-1, not kW. | feature_description.csv | 0 | 0 | 0.4951 | Values are NORMALISED to ~0-1 despite the documented unit.
sensor_31_avg | Grid reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -0.2882 | 0.4878 | SCALE INCONSISTENCY: _avg is normalised (-0.29..0.49) while _max/_min/_std are raw kVAr (-1002..1003). In 79.4% of rows _avg > _max, which is impossible in shared units.
sensor_31_max | Grid reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | maximum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -575.8 | 1003.3 | SCALE INCONSISTENCY: _avg is normalised (-0.29..0.49) while _max/_min/_std are raw kVAr (-1002..1003). In 79.4% of rows _avg > _max, which is impossible in shared units.
sensor_31_min | Grid reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | minimum | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | -1002.8 | 997.6 | SCALE INCONSISTENCY: _avg is normalised (-0.29..0.49) while _max/_min/_std are raw kVAr (-1002..1003). In 79.4% of rows _avg > _max, which is impossible in shared units.
sensor_31_std | Grid reactive power | kVAr | float64 | Electrical - reactive power | YES | NO | Grid / electrical | std_dev | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 575.7 | SCALE INCONSISTENCY: _avg is normalised (-0.29..0.49) while _max/_min/_std are raw kVAr (-1002..1003). In 79.4% of rows _avg > _max, which is impossible in shared units.
sensor_32_avg | Averaged voltage in phase 1 | V | float64 | Electrical - voltage | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 419.7
sensor_33_avg | Averaged voltage in phase 2 | V | float64 | Electrical - voltage | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 418.1
sensor_34_avg | Averaged voltage in phase 3 | V | float64 | Electrical - voltage | YES | NO | Grid / electrical | average | MEDIUM - phase imbalance in current/voltage indicates winding or connection faults. | feature_description.csv | 0 | 0 | 419.7
sensor_35_avg | Temperature measured by the IGBT-driver on the rotor side inverter phase1 | degC | float64 | Temperature | YES | NO | Converter | average | MEDIUM - converter thermal condition. | feature_description.csv | 0 | 24 | 98
sensor_36_avg | Temperature measured by the IGBT-driver on the rotor side inverter phase2 | degC | float64 | Temperature | YES | NO | Converter | average | MEDIUM - converter thermal condition. | feature_description.csv | 0 | 24 | 61
sensor_37_avg | Temperature measured by the IGBT-driver on the rotor side inverter phase3 | degC | float64 | Temperature | YES | NO | Converter | average | MEDIUM - converter thermal condition. | feature_description.csv | 0 | 24 | 104
sensor_38_avg | Temperature in HV transformer phase L1 | degC | float64 | Temperature | YES | NO | HV transformer | average | MEDIUM - directly targets the 1 Transformer failure. Phase spread is the meaningful quantity. | feature_description.csv | 0 | 28 | 107
sensor_39_avg | Temperature in HV transformer phase L2 | degC | float64 | Temperature | YES | NO | HV transformer | average | MEDIUM - directly targets the 1 Transformer failure. Phase spread is the meaningful quantity. | feature_description.csv | 0 | 28 | 122
sensor_40_avg | Temperature in HV transformer phase L3 | degC | float64 | Temperature | YES | NO | HV transformer | average | MEDIUM - directly targets the 1 Transformer failure. Phase spread is the meaningful quantity. | feature_description.csv | 0 | 27 | 137
sensor_41_avg | Temperature oil in hydraulic group | degC | float64 | Temperature | YES | NO | Hydraulic group | average | HIGH - the only direct observation of the hydraulic group, which is the failure mode in 6 of 12 documented anomalies. | feature_description.csv | 0 | 20 | 55
sensor_42_avg | Nacelle direction | deg | float64 | Wind / orientation | YES | NO | Nacelle | average | LOW/REFERENCE - internal reference temperature; nose cone tracks ambient closely. | feature_description.csv | 0 | 0 | 359 | ANGULAR - wraps at 360 deg; do not average or difference naively.
sensor_43_avg | Nacelle temperature | degC | float64 | Temperature | YES | NO | Nacelle | average | LOW/REFERENCE - internal reference temperature; nose cone tracks ambient closely. | feature_description.csv | 0 | 15 | 51
sensor_44 | Active power - generator disconnected | Wh | float64 | Electrical - active power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -5278 | 1416
sensor_45 | Active power - generator connected in delta | Wh | float64 | Electrical - active power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -1864 | 372865
sensor_46 | Active power - generator connected in star | Wh | float64 | Electrical - active power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 0 | 0 | CONSTANT ZERO across all 1,196,747 observations - no information. EXCLUDE.
sensor_47 | Reactive power - generator disconnected | VArh | float64 | Electrical - reactive power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -5849 | 3326
sensor_48 | Reactive power - generator connected in delta | VArh | float64 | Electrical - reactive power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -98475 | 166806
sensor_49 | Reactive power - generator connected in star | VArh | float64 | Electrical - reactive power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | 0 | 0 | CONSTANT ZERO across all 1,196,747 observations - no information. EXCLUDE.
sensor_50 | Total active power | Wh | float64 | Electrical - active power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -5367 | 371256
sensor_51 | Total reactive power | VArh | float64 | Electrical - reactive power | YES | NO | Not documented. | value | LOW - documented, but no direct link to a failure mode present in this dataset. | feature_description.csv | 0 | -98475 | 166806
sensor_52_avg | Rotor rpm | rpm | float64 | Speed (rotational) | YES | NO | Rotor / hub | average | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 14.9
sensor_52_max | Rotor rpm | rpm | float64 | Speed (rotational) | YES | NO | Rotor / hub | maximum | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 19.6
sensor_52_min | Rotor rpm | rpm | float64 | Speed (rotational) | YES | NO | Rotor / hub | minimum | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 14.8
sensor_52_std | Rotor rpm | rpm | float64 | Speed (rotational) | YES | NO | Rotor / hub | std_dev | MEDIUM - required to interpret every temperature. generator_rpm / rotor_rpm gives a gearbox-ratio integrity indicator (~113:1, std 0.42-0.45). | feature_description.csv | 0 | 0 | 7.4
sensor_53_avg | Temperature in the nose cone | degC | float64 | Temperature | YES | NO | Rotor / hub | average | LOW/REFERENCE - internal reference temperature; nose cone tracks ambient closely. | feature_description.csv | 0 | 6 | 47
time_offset_days | Timestamp correction applied to this event file | days | float64 | Metadata | NO | YES | Provenance | value | 0 for 20 files; 1.0 for events 40 and 71. | Derived in this project | 0 | 0 | 1
time_stamp_aligned | Timestamp moved onto the common Wind Farm A timeline | datetime | datetime64[ns] | Timestamp | NO | YES | Time index | value | Use this when merging event files. Events 40 and 71 carry a +1 day native offset. | Derived in this project | 0
turbine_uid | Turbine identifier used in this project | string | object | Identifier | NO | YES | Turbine | value | Grouping key for per-turbine models and splits. Never a feature. | Derived in this project | 0

## Status_Summary
Field | Value
-- WHAT IS status_type_id? --
Documented meaning | NOT DOCUMENTED. No supplied file defines the codes. No name is assigned to any code anywhere in this project.
Codes present | 0, 3, 4
-- DISTRIBUTION (deduplicated base) --
status_type_id == 0 | 367,728 (86.52%)
status_type_id == 3 | 9,909 (2.33%)
status_type_id == 4 | 47,386 (11.15%)
-- BY TURBINE (% of that turbine) --
A0 | code 0: 84.31% code 3: 2.70% code 4: 12.99%
A10 | code 0: 84.37% code 3: 2.62% code 4: 13.01%
A11 | code 0: 93.62% code 3: 1.12% code 4: 5.27%
A13 | code 0: 90.66% code 3: 1.80% code 4: 7.54%
A21 | code 0: 80.51% code 3: 3.29% code 4: 16.21%
-- EMPIRICAL BEHAVIOUR (measured, not documented) --
status 4 episode length | median 335.8 h; 19 of 24 episodes fall in 330-340 h (i.e. almost exactly 14 days)
status 3 episode length | median 72.0 h, and always immediately follows status 4
Interpretation | Such exact, repeated durations indicate the codes were stamped onto FIXED-LENGTH CONSTRUCTED WINDOWS, not recorded live.
-- RELATIONSHIP TO THE EVENT LABEL --
Inside anomaly events | 95.04% status 4, 4.66% status 0
Inside normal events | 100.00% status 0
status 4 outside any labelled event | 69.07% of all status-4 observations
status-4 episodes overlapping an anomaly | 11 of 24
-- WHY IT CANNOT BE THE ML TARGET --
Reason 1 | The rule 'anomaly if status_type_id == 4' alone reproduces 95% of anomaly-event observations and 0% of normal-event observations. A model given it would report meaningless near-perfect accuracy.
Reason 2 | For 8 of 12 anomalies it is already active 7 days BEFORE event_start - it encodes the answer rather than predicting it.
Reason 3 | Its meaning is undocumented, and 69% of status-4 time is unlabelled, which contradicts a simple '4 = failure' reading.
PERMITTED USE | As a FILTER ONLY - select status_type_id == 0 rows to train a normal-behaviour model. Never as a feature. Never as the target.

## Event_Summary
event_id | turbine_uid | asset | event_label | event_description | event_start_aligned | event_end_aligned | event_duration_h | event_start | event_end | time_offset_days | event_start_id | event_end_id | window_start | window_end | pred_start | pred_end | source_file | excel_copy
71 | A0 | 0 | normal |  | 2023-01-01 | 2023-01-15 | 336 | 2023-01-02 | 2023-01-16 | 1 | 52439 | 54455 | 2021-12-31 00:00:00 | 2023-01-17 00:00:00 | 2022-12-31 00:00:00 | 2023-01-17 00:00:00 | datasets/71.csv | cleaned_data/excel/event_71.xlsx
24 | A0 | 0 | normal |  | 2023-04-27 15:00 | 2023-05-11 11:20 | 332.3333 | 2023-04-27 15:00 | 2023-05-11 11:20 | 0 | 52720 | 54714 | 2022-04-24 15:00:00 | 2023-05-13 11:20:00 | 2023-04-24 15:00:00 | 2023-05-13 11:20:00 | datasets/24.csv | cleaned_data/excel/event_24.xlsx
73 | A0 | 0 | anomaly | Hydraulic group | 2023-06-10 11:40 | 2023-06-17 11:40 | 168 | 2023-06-10 11:40 | 2023-06-17 11:40 | 0 | 52745 | 53753 | 2022-06-07 11:40:00 | 2023-06-19 11:40:00 | 2023-06-07 11:40:00 | 2023-06-19 11:40:00 | datasets/73.csv | cleaned_data/excel/event_73.xlsx
0 | A0 | 0 | anomaly | Generator bearing failure | 2023-08-06 06:10 | 2023-08-20 06:10 | 336 | 2023-08-06 06:10 | 2023-08-20 06:10 | 0 | 52436 | 54447 | 2022-08-04 06:10:00 | 2023-08-24 06:10:00 | 2023-08-04 06:10:00 | 2023-08-24 06:10:00 | datasets/0.csv | cleaned_data/excel/event_0.xlsx
26 | A0 | 0 | anomaly | Hydraulic group | 2023-10-12 10:20 | 2023-10-19 10:20 | 168 | 2023-10-12 10:20 | 2023-10-19 10:20 | 0 | 52261 | 53269 | 2022-10-12 10:20:00 | 2023-10-22 10:20:00 | 2023-10-12 10:20:00 | 2023-10-22 10:20:00 | datasets/26.csv | cleaned_data/excel/event_26.xlsx
40 | A10 | 10 | anomaly | Generator bearing failure | 2022-12-25 | 2023-01-25 13:00 | 757 | 2022-12-26 | 2023-01-26 13:00 | 1 | 51363 | 55870 | 2021-12-31 00:00:00 | 2023-01-27 13:00:00 | 2022-12-24 00:00:00 | 2023-01-27 13:00:00 | datasets/40.csv | cleaned_data/excel/event_40.xlsx
3 | A10 | 10 | normal |  | 2023-04-27 03:00 | 2023-05-18 01:10 | 502.1667 | 2023-04-27 03:00 | 2023-05-18 01:10 | 0 | 52185 | 55198 | 2022-04-27 03:00:00 | 2023-05-20 01:10:00 | 2023-04-27 03:00:00 | 2023-05-20 01:10:00 | datasets/3.csv | cleaned_data/excel/event_3.xlsx
42 | A10 | 10 | anomaly | Hydraulic group | 2023-09-09 15:50 | 2023-09-16 15:50 | 168 | 2023-09-09 15:50 | 2023-09-16 15:50 | 0 | 52303 | 53309 | 2022-09-09 15:50:00 | 2023-09-20 15:50:00 | 2023-09-09 15:50:00 | 2023-09-20 15:50:00 | datasets/42.csv | cleaned_data/excel/event_42.xlsx
10 | A10 | 10 | anomaly | Gearbox failure | 2023-10-11 08:40 | 2023-10-18 08:40 | 168 | 2023-10-11 08:40 | 2023-10-18 08:40 | 0 | 52611 | 53591 | 2022-10-09 08:40:00 | 2023-10-18 08:40:00 | 2023-10-09 08:40:00 | 2023-10-18 08:40:00 | datasets/10.csv | cleaned_data/excel/event_10.xlsx
17 | A10 | 10 | normal |  | 2023-11-02 15:20 | 2023-11-16 00:40 | 321.3333 | 2023-11-02 15:20 | 2023-11-16 00:40 | 0 | 52597 | 54513 | 2022-10-31 15:20:00 | 2023-11-20 00:40:00 | 2023-10-31 15:20:00 | 2023-11-20 00:40:00 | datasets/17.csv | cleaned_data/excel/event_17.xlsx
92 | A11 | 11 | normal |  | 2023-04-05 02:30 | 2023-04-14 10:00 | 223.5 | 2023-04-05 02:30 | 2023-04-14 10:00 | 0 | 52437 | 53778 | 2022-04-04 02:30:00 | 2023-04-16 10:00:00 | 2023-04-04 02:30:00 | 2023-04-16 10:00:00 | datasets/92.csv | cleaned_data/excel/event_92.xlsx
25 | A11 | 11 | normal |  | 2023-05-23 06:50 | 2023-06-05 02:30 | 307.6667 | 2023-05-23 06:50 | 2023-06-05 02:30 | 0 | 52289 | 54135 | 2022-05-23 06:50:00 | 2023-06-09 02:30:00 | 2023-05-23 06:50:00 | 2023-06-09 02:30:00 | datasets/25.csv | cleaned_data/excel/event_25.xlsx
68 | A11 | 11 | anomaly | Transformer failure | 2023-07-28 13:20 | 2023-08-11 13:10 | 335.8333 | 2023-07-28 13:20 | 2023-08-11 13:10 | 0 | 52063 | 54076 | 2022-07-28 13:20:00 | 2023-08-13 13:20:00 | 2023-07-28 13:20:00 | 2023-08-13 13:20:00 | datasets/68.csv | cleaned_data/excel/event_68.xlsx
69 | A11 | 11 | normal |  | 2023-09-04 00:50 | 2023-09-18 00:50 | 336 | 2023-09-04 00:50 | 2023-09-18 00:50 | 0 | 52364 | 54380 | 2022-09-03 00:50:00 | 2023-09-21 00:50:00 | 2023-09-03 00:50:00 | 2023-09-21 00:50:00 | datasets/69.csv | cleaned_data/excel/event_69.xlsx
14 | A13 | 13 | normal |  | 2023-03-05 14:00 | 2023-03-12 18:40 | 172.6667 | 2023-03-05 14:00 | 2023-03-12 18:40 | 0 | 52584 | 53620 | 2022-03-03 14:00:00 | 2023-03-16 18:40:00 | 2023-03-03 14:00:00 | 2023-03-16 18:40:00 | datasets/14.csv | cleaned_data/excel/event_14.xlsx
45 | A13 | 13 | anomaly | Hydraulic group | 2023-04-19 18:10 | 2023-04-26 18:10 | 168 | 2023-04-19 18:10 | 2023-04-26 18:10 | 0 | 52731 | 53738 | 2022-04-16 18:10:00 | 2023-04-26 18:10:00 | 2023-04-16 18:10:00 | 2023-04-26 18:10:00 | datasets/45.csv | cleaned_data/excel/event_45.xlsx
38 | A13 | 13 | normal |  | 2023-07-01 15:40 | 2023-07-15 07:40 | 328 | 2023-07-01 15:40 | 2023-07-15 07:40 | 0 | 52723 | 54546 | 2022-06-28 15:40:00 | 2023-07-17 07:40:00 | 2023-06-28 15:40:00 | 2023-07-17 07:40:00 | datasets/38.csv | cleaned_data/excel/event_38.xlsx
84 | A13 | 13 | anomaly | Hydraulic group | 2023-09-05 15:30 | 2023-09-12 15:30 | 168 | 2023-09-05 15:30 | 2023-09-12 15:30 | 0 | 52623 | 53627 | 2022-09-03 15:30:00 | 2023-09-13 15:30:00 | 2023-09-03 15:30:00 | 2023-09-13 15:30:00 | datasets/84.csv | cleaned_data/excel/event_84.xlsx
13 | A21 | 21 | normal |  | 2023-05-03 13:20 | 2023-05-24 10:20 | 501 | 2023-05-03 13:20 | 2023-05-24 10:20 | 0 | 50859 | 53865 | 2022-04-30 13:20:00 | 2023-05-25 10:20:00 | 2023-04-30 13:20:00 | 2023-05-25 10:20:00 | datasets/13.csv | cleaned_data/excel/event_13.xlsx
22 | A21 | 21 | anomaly | Hydraulic group | 2023-08-12 09:50 | 2023-08-19 10:00 | 168.1667 | 2023-08-12 09:50 | 2023-08-19 10:00 | 0 | 51888 | 52892 | 2022-08-12 09:50:00 | 2023-08-20 09:50:00 | 2023-08-12 09:50:00 | 2023-08-20 09:50:00 | datasets/22.csv | cleaned_data/excel/event_22.xlsx
51 | A21 | 21 | anomaly | Gearbox bearings damaged | 2023-10-06 01:30 | 2023-10-17 16:10 | 278.6667 | 2023-10-06 01:30 | 2023-10-17 16:10 | 0 | 52331 | 54003 | 2022-10-04 01:30:00 | 2023-10-20 16:10:00 | 2023-10-04 01:30:00 | 2023-10-20 16:10:00 | datasets/51.csv | cleaned_data/excel/event_51.xlsx
72 | A21 | 21 | anomaly | Gearbox failure | 2023-10-10 08:40 | 2023-10-17 08:40 | 168 | 2023-10-10 08:40 | 2023-10-17 08:40 | 0 | 52497 | 53505 | 2022-10-07 08:40:00 | 2023-10-21 08:40:00 | 2023-10-07 08:40:00 | 2023-10-21 08:40:00 | datasets/72.csv | cleaned_data/excel/event_72.xlsx

## Time_Coverage
month | A0 | A10 | A11 | A13 | A21 | TOTAL
2021-12 | 144 | 144 | 0 | 0 | 0 | 288
2022-01 | 4464 | 4464 | 0 | 0 | 0 | 8928
2022-02 | 4032 | 4032 | 0 | 0 | 0 | 8064
2022-03 | 4454 | 4451 | 0 | 4083 | 0 | 12988
2022-04 | 4320 | 4320 | 3873 | 4320 | 64 | 16897
2022-05 | 4439 | 4428 | 4439 | 4438 | 4439 | 22183
2022-06 | 4318 | 4303 | 4318 | 4318 | 4318 | 21575
2022-07 | 4464 | 4450 | 4460 | 4450 | 2868 | 20692
2022-08 | 4315 | 4286 | 4288 | 4286 | 4315 | 21490
2022-09 | 4302 | 4288 | 4301 | 4320 | 4301 | 21512
2022-10 | 4431 | 4428 | 4429 | 4430 | 4328 | 22046
2022-11 | 4292 | 4313 | 4320 | 4320 | 4122 | 21367
2022-12 | 4464 | 4460 | 4464 | 4464 | 4464 | 22316
2023-01 | 4454 | 4419 | 4464 | 4463 | 4464 | 22264
2023-02 | 4032 | 4032 | 4032 | 4032 | 4032 | 20160
2023-03 | 4458 | 4458 | 4458 | 4458 | 4458 | 22290
2023-04 | 4319 | 4320 | 4320 | 4319 | 4318 | 21596
2023-05 | 4464 | 4464 | 4435 | 4440 | 4464 | 22267
2023-06 | 4303 | 4309 | 4303 | 4309 | 4303 | 21527
2023-07 | 4316 | 4319 | 4247 | 4319 | 4319 | 21520
2023-08 | 4415 | 4461 | 4447 | 4461 | 4454 | 22238
2023-09 | 4291 | 4318 | 2886 | 1818 | 4317 | 17630
2023-10 | 3087 | 4436 | 0 | 0 | 2933 | 10456
2023-11 | 0 | 2729 | 0 | 0 | 0 | 2729

## Derivable_Later
Field | Value
-- WHAT PHASE 3 CAN DERIVE (NOT COMPUTED YET) --
Rolling statistics | Rolling mean / std / min / max over 6 h, 24 h and 7 d windows.
Rate of change | First difference and slope of temperatures over time.
Variability | Within-interval spread is already supplied as _std columns.
Temperature rise over ambient | sensor - sensor_0_avg. Removes seasonal effect.
Component temperature differences | Generator bearing DE minus NDE; gearbox bearing minus gearbox oil. Self-normalising - they cancel ambient and load.
Phase spread | max minus min across the three stator phases (15/16/17) and the three transformer phases (38/39/40). Imbalance indicates a fault.
Gearbox ratio integrity | generator_rpm / rotor_rpm. Verified as a tight mechanical constant near 113:1 in normal operation.
Power-curve deviation | Actual power minus expected power at the same wind speed.
Operating-condition normalisation | Residual of a sensor against its expected value at the same power / speed / ambient bin.
Normal-behaviour-model residuals | The central Phase 3 health signal.
-- WHAT CANNOT BE DERIVED FROM THIS DATA --
Vibration features | No vibration channel exists.
Pressure features | No pressure channel exists.
Remaining useful life | No run-to-failure or degradation-stage labelling.
Guaranteed failure lead time | 10 of 12 anomalies have no normal-operation data before event_start; labelled horizon is 0-72 h.
Maintenance due date / repair action | No maintenance or work-order records exist.

## Leakage_Rules
Field | Value
-- MUST NEVER ENTER THE ML FEATURE MATRIX --
status_type_id | Near-perfect label proxy. Filter only.
train_test | Per-event-window metadata; 38,406 timestamps carry both values.
row_id_in_event (raw 'id') | Per-file counter encoding position in the window.
event_id | Provenance key - identifies the event directly.
asset_id / turbine_uid | Grouping keys. A model could memorise which turbine has more anomalies. Use for splitting only.
time_stamp / calendar features | All 22 events fall in 2023 and anomalies cluster seasonally; the model would learn WHEN labelled events happen. Ordering and splitting only.
sensor_46, sensor_49 | Constant zero - no information.
Raw un-normalised temperatures | The strongest apparent 'precursor' in this data is ambient temperature. Condition on operating point first.
Any row at or after event_start of the scored window | Direct future leakage.
Global scalers / PCA fitted on all data | Fit on the training partition of each fold only.
-- SCALE TRAP (not leakage, but will corrupt features) --
sensor_31_avg vs _max/_min/_std | _avg is normalised (-0.29..0.49); _max/_min/_std are raw kVAr (-1002..1003). _avg > _max in 79.4% of rows. Do not mix them in one feature group.
power_29 / power_30 / reactive_power_27 / reactive_power_28 | Normalised to ~0-1 despite documented kW/kVAr units. There is no physical kW scale.

## Data_Files
event_id | raw_file | represents | turbine_uid | asset_id | event_label | event_description | timestamp_offset_days | excel_inspection_copy
0 | datasets/0.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A0 | 0 | anomaly | Generator bearing failure | 0 | cleaned_data/excel/event_0.xlsx
3 | datasets/3.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A10 | 10 | normal |  | 0 | cleaned_data/excel/event_3.xlsx
10 | datasets/10.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A10 | 10 | anomaly | Gearbox failure | 0 | cleaned_data/excel/event_10.xlsx
13 | datasets/13.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A21 | 21 | normal |  | 0 | cleaned_data/excel/event_13.xlsx
14 | datasets/14.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A13 | 13 | normal |  | 0 | cleaned_data/excel/event_14.xlsx
17 | datasets/17.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A10 | 10 | normal |  | 0 | cleaned_data/excel/event_17.xlsx
22 | datasets/22.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A21 | 21 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_22.xlsx
24 | datasets/24.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A0 | 0 | normal |  | 0 | cleaned_data/excel/event_24.xlsx
25 | datasets/25.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A11 | 11 | normal |  | 0 | cleaned_data/excel/event_25.xlsx
26 | datasets/26.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A0 | 0 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_26.xlsx
38 | datasets/38.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A13 | 13 | normal |  | 0 | cleaned_data/excel/event_38.xlsx
40 | datasets/40.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A10 | 10 | anomaly | Generator bearing failure | 1 | cleaned_data/excel/event_40.xlsx
42 | datasets/42.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A10 | 10 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_42.xlsx
45 | datasets/45.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A13 | 13 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_45.xlsx
51 | datasets/51.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A21 | 21 | anomaly | Gearbox bearings damaged | 0 | cleaned_data/excel/event_51.xlsx
68 | datasets/68.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A11 | 11 | anomaly | Transformer failure | 0 | cleaned_data/excel/event_68.xlsx
69 | datasets/69.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A11 | 11 | normal |  | 0 | cleaned_data/excel/event_69.xlsx
71 | datasets/71.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A0 | 0 | normal |  | 1 | cleaned_data/excel/event_71.xlsx
72 | datasets/72.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A21 | 21 | anomaly | Gearbox failure | 0 | cleaned_data/excel/event_72.xlsx
73 | datasets/73.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A0 | 0 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_73.xlsx
84 | datasets/84.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A13 | 13 | anomaly | Hydraulic group | 0 | cleaned_data/excel/event_84.xlsx
92 | datasets/92.csv | EVENT WINDOW (filename == event_id, NOT a turbine id) | A11 | 11 | normal |  | 0 | cleaned_data/excel/event_92.xlsx